## Slide 2: WE ARE JSW STEEL
ATRUEVISIONARY. ALEGENDARYINDUSTRIALIST.A GREAT PHILANTHROPIST.
ALEGACYTHATWILLALWAYSBECHERISHED.
SHRI. O. P. JINDAL
07.08.1930 - 31.03.2005
Founder and Visionary, O. P. Jindal Group
JSWSteel is oneof India’s leading integrated andgeographically diverse steel manufacturers. Ourgoal is to partner in India’s growthstory by supplying steel forvital infrastructure projects, providing value added steel solutions through innovationwhile investing in sustainability and improving the well-being ofthe broader community.
Wehave adoptedadvanced technologies and processes to ensure that steel continues to be the preferred material as we transition towardsa low-carbon future. Inpursuing ourstrategic objectives, we are committedto responsibly reducing our environmental footprint andpositivelyinfluencing the lives of ouremployees and partners.
28.2 MTPA
Domesticcrude
steel capacity
50 MTPA
Expected domestic capacity by FY2030-31
~13.5 MTPA Domestic downstream steel capacity *Includes JSW Steel Coated Products Ltd., Vijayanagar CRM Complex and BPSL | 1.5 MNTPA (Crude Steel Capacity) International presence JSWSteel USA | 364 Brandedstores added in FY 2023-24
100+ Countries (export footprint) | 24 Captiveiron ore mines | 03 Captive coking coal mines
 | 25,550 Direct employees JSWSteel consolidated | 

## Slide 3
EXPANDING
CAPACITIES AND CAPABILITIES
USA
Manufacturing facilities
Vijayanagar
Salem
Salav
Dolvi
Sambalpur
Expecteddomestic capacityby FY2030-31
Bawal
Dhar
Anjar
Kalmeshwar
Raigarh
Raipur
Vasind & Tarapur
Khopoli
Rajpura
Downstream facilities Mines
International manufacturing units
INDIA
Manufacturing Facilities
Vijayanagar Works (ISP)
P
Hot Rolled (HR), Cold Rolled (CR), Galvanised (GI) and Galvalume (GL), colour-coated products, wire rods, TMT
C
12.5 MTPA crude steel
5 MTPAunder commissioning, further addition
of 1.5 MTPAby FY2024-25
Bhushan Powerand Steel Ltd. Sambalpur
P
HR, CR, Galvanised (GI) and Galvalume (GL), colour- coated products, TMT, slabs, billets, cable tape, black pipe, precision tubes
C
3.5 MTPA crude steel
1.5 MTPAunder commissioning in phases
Dolvi Works (ISP)
P
HR,TMT
C
10 MTPA crude steel
further addition of
5 MTPAby FY 2027-28
Mivaan Steels Limited, Raipur
P
Billets, Ferro alloys, Structures
C
0.25 MTPA crude steel
Salav Works
P
Direct Reduced Iron (DRI) / Hot Briquetted Iron (HRI)
C
0.9 MTPA DRI/HBI
Salem Works (ISP)
P
Wirerod, alloy long products, billets/blooms
C
1 MTPA crude steel
Raigarh Works
P
Rebars, alloy special steel products, slabs, billets
C
0.95 MTPA crude steel
Operational iron ore mines
50 MTPA
Ohio
Key Products Capacity
Baytown
Piombino
ITALY
INTERNATIONAL
Organisational Overview
OPERATIONS AND PRESENCE

## Slide 4: BPSL - Facilities and Capacities Overview
2.75
4.50
5.00
FY22
Current
FY25
Raw Material Processing
Coke Oven Pellet Plant Sinter Plant
Captive Power Plant
Iron and Steel
1.80
2.35
DRI
Blast Furnaces
Steel Melting Shop
Value Addition
CRCA / CRFH GI / GL
PPGI / PPGL
Alloy Steel Bars Pipes & Tubes
3.50
Chandigarh
Cold Rolled Steel Strips and Precision Tubes
Sambalpur
Integrated Steel Plant with Captive Power Plant
Netrabandha
Iron Ore Mine: 82mt Reserves
Kolkata
Value added: CRCA, GI/GL
Crude Steel Capacity
4.50 mtpa
Downstream Capacity
1.7 mtpa
Expansion Plan

## Slide 5
AtJSW,our visionisto actively contributeto society's developmentin a socially, ethically, and environmentally responsiblemanner. Ourgoal is to ensurethat ouractions support meetingthe needs of all, without compromisingthe ability of future generations to meet their ownneeds
Mainstreaming sustainability across the businesses
CAPITALS DEPLOYED F Financial Capital I Intellectual Capital M Manufactured Capital CAPITALS ENHANCED S Social and Relationship Capital N Natural Capital H Human Capital
28% CO2 emissions from base year
Climate Change
Targeting Net Neutral by 2050
42%
of CO2 emission intensity to
1.95 tCO2/tcs by 2030, aligned
with India’s NDCs
Energy Transition
Transition from thermal to renewable energy (RE)- installation of 10 GW REcapacities by 2030
19%
in specific energy consumption to 5.65 Gcal/tcs by 2030
Water Security
Maintaining zero liquid discharge
39%
in specific water consumption to 2.21 m3/tcs by 2030
Water neutrality at coated steel plants by 2030
Diversity and Safety
Aim to be recognized as one of the world's safest organization by 2030
Achieving 33% women representation at the general engineering and management trainee levels by 2030
Air Emissions
PM, SOxand NOx emission targets of 0.26, 0.82 and
0.91 kg/tcs respectively,
by 2030
Circularity and Biodiversity
100% recycling of all waste generated from operations
‘No net loss’ of Biodiversity by 2030
Our commitments

## Slide 6: Targeting Net Zero by 2050
Ensuring Energy Efficiency
Renewable Power (Energy Transition)
Actively Improving Material Quality
Utilizing Alternative Fuel Sources
Increase in Scrap (Material Circularity)
Commercial Deployment of Green Hydrogen for Steelmaking
Scrap-based EAF
Use of Syngas & TGR1 in BF (Carbon Circularity)
Large Scale Implementation of CCUS2
Carbon Offsetting
Short-Term
Medium and Long-Term
Increasing Demand-side Material Efficiency
Enhancing Process Efficiency
Nature Based Solutions
Alternate Steel-making Technologies, e.g. Electrolysis

## Slide 7: Our focus areas and performance
Focus Areas
KPIs
Units
FY 2023-24
FY 2022-23
FY 2021-22
FY 2020-21
Climate Change
CO2 emissions (Scope 1 and 2)
‘000 tCO
2
53,167
49,359
44,211
37,523
CO2 emissionintensity(Scope 1 and 2) tCO2/tcs
2.44
2.36
2.50
2.49
Waste
Airemissions
Specific energy consumption Energy Energy consumptionwithin |  |  | Gcal/tcs million GJ | 5.68 517.69 | 5.66 494.38 | 6.04 446.78 | 6.38 402.53
the organisation |  |  |  |  |  |  | 
Specificiron ore consumption |  |  | t/tcs | 1.57 | 1.58 | 1.82 | 1.68
Resources Specific coal consumption |  |  | t/tcs | 0.74 | 0.74 | 0.67 | 0.69
Specific freshwater consumption |  |  | m3/tcs | 2.39 | 2.45 | 2.45 | 2.41
Water Resources | (Forsteel production) |  |  |  |  |  | 
 | Non-hazardouswaste generated |  | ‘000 tonne | 15,070 | 14,278 | 13,157 | 11,968
 | Hazardous waste generated |  | ‘000 tonne | 141.00 | 136.25 | 122.9 | 84.62
 | Waste recycled | % |  | 99.11 | 99.77 | 100 | 92.67
Wastewater | Wastewater recycled |  | ‘000 m3 | 22,557 | 20,782 | 16,539 | 16,050
 | Particulate matter |  | kg/tcs | 0.38 | 0.42 | 0.488 | 0.48
 | SOx |  | kg/tcs | 1.66 | 1.69 | 1.895 | 2.05
 | NOx |  | kg/tcs | 1.19 | 1.19 | 1.26 | 1.52
Biodiversity | Saplings planted |  | Nos.(lakh) | 3.5 | 3.5 | 3.5 | 1.5
INNOVATING FOR GREENER TOMORROW

## Slide 8
3.85 to 3.76 T/ MWh
SSC reduction
105 MW to 115 MW
MW Optimization
Reduction in 4,553 tCO2
emissions
13.10% to 12..60 %
APC reduction
Energy saved
throttlingloss
Reduction in 1,366 tCO2
emissions
2 KL per lit-up
LDO usages Saved
113. lacs
Cost Saving
Reduction in 76 tCO2 emissions
3 MW/day
Power saving
44.6 lacs
Cost saving
Reduction in 683 tCO2 emissions
1.4 MW/day
Power saving
31.5 lacs
Cost saving
Reduction in 327 tCO2 emissions
82.2 lacs
Cost saving
Reduction in 847 tCO2 emissions
Micro turbine 3.5 MW
LDO Consumption Optimization
Tunning fork level switch
PA fan air friction reduction
BFP
Destaging
TG-1(130 MW COH
75
ESG Score
A-
Climate Change
A
Water Security
Onlysteelmaker globallywith Aratingin Water Security
Ratings
FY 2023-24 ENCON HIGHLIGHTS
7
3.7 MW/day
Power saving
OUR VALUE IMPACT

## Slide 9: Energy Conservation Journey
2019
2024
2020
2023
2021
BFP ARC valve repairing
DMCC Impeller trimming
Condenseronlinetube cleaning system
CEP Stagetrimming
Boiler overhauling
APH tubereplacement
Turbine Overhauling
Boilermajor
overhauling
ESP modification
PA canopy
modification
2022
CILMS implementation
Microturbine
Implementation of PMS for plant performance assessment diagnostic optimization
Installation of Micro turbine at
PRDS station
Tunning fork type level switch in ESP hoppers reduces APC 3MW/day in CFBC & WHRB
High energy drain valve
Additional CE & DE fields in ESP
ESP new TR set

## Slide 10
15.47%
14.50%
14.10%
13%
11%
10.00%
8.00%
6.00%
4.00%
2.00%
0.00%
12.00%
18.00%
16.00%
14.00%
Aux.Power
FY-21 FY-22 FY-23 FY-24 FY-25
12.72

## Slide 11: ESG Dashboard
1.95
2.44
2.36
2.50
2.49
2.52
2.75
2.59
3.39
FY 30
FY 24
FY 23
FY 22
FY 21
FY 20
FY 19
FY 18
FY 05
tCO2/tcs
2005 to 2030: 42% ↓
2024 to 2030: 20% ↓
5.65
5.68
5.66
6.04
6.38
6.56
6.24
6.59
6.94
FY 30
FY 24
FY 23
FY 22
FY 21
FY 20
FY 19
FY 18
FY 05
GCal/tcs
2005 to 2030: 19% ↓
2024 to 2030: 0.6%↓
100%
99.11%
99.77%
100%
93%
62%
FY 30
FY 24
FY 23
FY 22
FY 21
FY 05
%
2005 to 2030: 38 pp ↑
2.21
2.39
2.45
2.45
2.41
2.60
3.79
4.13
3.60
FY 30
FY 24
FY 23
FY 22
FY 21
FY 20
FY 19
FY 18
FY 05
m3/tcs
2005 to 2030: 39% ↓
2024 to 2030: 8% ↓
0.91
1.19 1.19
1.26
1.52
1.36
1.29
1.24
0.82
1.69
1.69
1.60
FY 18 FY 19 FY 20 FY 21 FY 22 FY 23 FY 24 FY 30
Specific NOx Emission Intensity
Specific SOx Emission Intensity
2.05
1.88 1.89
1.74
kg/tcs
2024 to 2030
Specific NOx Emission Intensity: 24% ↓ Specific SOx Emission Intensity: 51% ↓
0.26
0.38
0.42
0.49
0.48
0.98
0.94
0.98
0.93
FY 30
FY 24
FY 23
FY 22
FY 21
FY 20
FY 19
FY 18
FY 05
kg/tcs
2005 to 2030: 72% ↓
2024 to 2030: 31% ↓
Environment

## Slide 12: Social
13,301
12,856
12,398
12,481
12,954
11,266
11,619
FY 24
FY 23
FY 22
FY 21
FY 20
FY 19
FY 18
number
6,682
6,110
5,466
5,588
5,363
5,062
4,398
FY 24
FY 23
FY 22
FY 21
FY 20
FY 19
FY 18
number
6,619
6,746
6,932
6,893
7,591
6,868
6,557
FY 24
FY 23
FY 22
FY 21
FY 20
FY 19
FY 18
number
858
743
666
639
659
403
480
FY 24
FY 23
FY 22
FY 21
FY 20
FY 19
FY 18
number
24
23
28
32
40
32
19
FY 24
FY 23
FY 22
FY 21
FY 20
FY 19
FY 18
number
0.095
0.20
0.32
0.26
0.32
0.36
0.43
FY 24
FY 23
FY 22
FY 21
FY 20
FY 19
FY 18
per million manhours

## Slide 13: Water intensive industries in focus
264
526
1400
3647
0
1000
2000
4000
3000
Thermal Power Plants
Pulp & Paper Industries
Textiles Industries
Iron & Steel Industries
No. of Industries
Engineering, 5.05% Pulp & Paper, 2.26% Textiles, 2.07%
Steel, 1.29%
Sugar, 0.49%
Fertilizers, 0.18%
Others, 0.78%
Thermal Power Plant, 87.87%

## Slide 14: Consumption Areas of Water in Power Plant
used
in
almost all
areas/ facilities of
Water is thermal
power stations in one way or other. A
typical list of plant systems/ applications requiring consumptive water is indicated as below:
Cooling water system (Condenser & ACW)
Ash handling system
Power cycle make up
Coal dust suppression system
Service water system
Potable water system
Gardening
Evaporation from raw water reservoir

## Slide 15: Processes & water usage areas in a thermal power plant
Filter House
Auxiliary uses
Drinking water Supply
(Township & Plant)
Raw Water Treatment
Cooling Towers IDCT
Power Generation Units
Makeup Water
Closed cycle Water Recirculation
DM Plant
Fire Fighting
Ash Handling System
Boilers
Condenser
Steam
Turbines
Feed water
Ash Dyke
Main Intake Water Reservoir
Coal Handling
Ash water recirculation
Evaporative + Drift Losses

## Slide 16: Typical Water Consumption Figures
Plant water consumption is governed by a number of factors such as :
Quality of raw water, type of condenser cooling system, Quality of coal, Ash utilization, Type of ash disposal system, Waste water management aspects etc.
In the past, power stations were designed with water systems having liberal considerations and high design margins.
The consumptive water requirement for coal based plants with cooling towers used to be about 7 m3/h per MW
In recent times, plants have been designed with reduced Plant water consumption rate in the range 3.5 - 4 m3/h per MW

## Slide 17: Cooling Water System
Cooling Systems in Practice in India:
Cooling Tower (IDCT / NDCT) – Wet Cooling
Air Cooled Condenser – Dry Cooling
Once Through Cooling – To be replaced as per Dec 7, 2015 Notification

## Slide 18: Dry Cooling System
TURBINE
GENERATOR
CONDENSER
FAN
CONDESATE
STEAM
PUMP
AIR IN
AIR IN
AIR OUT
AIR OUT

## Slide 19: Economics of Dry Cooling vs Wet Cooling System
50
Initial Cost (Rs Crore)
150
120
Wet Cooling - IDCT Wet Cooling - NDCT Dry Cooling - ACC
For a typical 660 MW Coal Based TPP
*Considering Steam cycle efficiency as 40%

## Slide 20: Space Requirement of Dry Cooling vs Wet Cooling System(NDCT & IDCT)
8000
Foot Print Area (Sq M)
15000
14000
Wet Cooling - IDCT Wet Cooling - NDCT Dry Cooling - ACC
For a typical 660 MW Coal Based TPP
*Considering Steam cycle efficiency as 40%

## Slide 21: Power Consumption of Dry Cooling vs Wet Cooling System
Aux. Power Consumption* (KW)
8000
6500
5000
Wet Cooling - IDCT Wet Cooling - NDCT Dry Cooling - ACC
For a typical 660 MW Coal Based TPP
*Considering above plan area.
#CW Pump Power included for IDCT & NDCT.

## Slide 22: Water Consumption Comparison of Dry Cooling vs Wet Cooling System
1.60%
1.60%
0.05%
0.75%
0.05%
0.75%
IDCT
Water Losses as ‘%’ Circulating Water Flow
Evaporation Loss Blowdown Loss Drift Loss
0
NDCT ACC
For a typical 660 MW Coal Based TPP
*Considering Steam cycle efficiency as 40% and COC=3.0

## Slide 23: Water Conservation Techniques for CW System
Replace Once Through Cooling System with Cooling Towers / Air Cooled Condensers
Implementation of High operating COC (Cycles of Concentration) to reduce the blow-down loss
Increasing COCto 5 from COC=3.0, Blow-downloss willreduce by 50%.
Installation of Air Cooled Condensers

## Slide 24: Techno- economics of Dry & Wet Cooling Systems
102
100
98
96
94
92
90
88
IDCT
NDCT
ACC
As compared to wet cooling system, dry condenser cooling system results in reduction of unit output by about 7%
Unit Output (%)
Unit Output (%)

## Slide 25: Techno- economics of Dry & Wet Cooling Systems
The heat rate of the unit with dry condenser cooling system is higher by about 7% in accordance with reduced output as indicated.
Heat Rate on ACC
In terms of efficiency, thermal efficiency of the plant shall reduce by about
2.5 percentage points
Plant Thermal efficiency with dry Cooling system
7%
2.5%

## Slide 26: Techno- economics of Dry & Wet Cooling Systems
Specific coal consumption of the unit shall increase by about 7%.
Specific coal
consumption with dry Cooling system
Typical CO2 emission from the plant shall also increase by about 7% (from 0.9 kg/kWh to 0.96 kg/kWh) with dry cooling system as compared to wet cooling system.
Specific CO2 emission with dry Cooling system
7%
7%

## Slide 27: Techno- economics of Dry & Wet Cooling Systems
7
6.8
6.6
6.4
6.2
6
5.8
5.6
IDCT
NDCT
ACC
For a conventional 500 MW unit, Aux Power Consumption is 6.5 % with IDCT, 6 % with NDCT based CW system and 6.8 % of gross output for plant with direct cooling air cooled condensers
Plant Auxiliary Power Consumption (% of Rated Plant Output)
Auxiliary Power Consumption (% of Rated Output)

## Slide 28: Techno- economics of Dry & Wet Cooling Systems
Cost for plant with wet cooling system as ` 5 crore/MW, the cost of the plant with dry cooling system would vary from ` 5.5 to 5.7 crore/MW
Cost of Plant with dry Cooling system
The levelised tariff is expected to increase by about 8- 9% over base levelised tariff for plant with dry Cooling system
Levelised Tariff with dry Cooling system
10%
8-9%

## Slide 29: Steam & Water Analysis System-SWAS

## Slide 30: AVGF- Auto Valve less Gravity Filter
5-10 %
AVGF
MCW COOLING TOWER
HOT WATER
COLD WATER CONDENSER
ETP
45 m³ BACK WASH WATER RECYCLED

## Slide 31: General Fundamentals
Cooling Tower – A medium for Heat Transfer
The make-up water source is used to replenish water lost by evaporation. In a re-circulating cooling system, concentration of mineral ions in water continuously increases due to water evaporation.
For every 6ºC decrease in temperature across the tower, approximately 1% of the circulation water will be evaporated, thus increasing the dissolved solids content of water in the system.
When the concentrated water is heated inside heat transfer equipment, the calcium and bicarbonate ions precipitate due to the changes in solubility, forming hard scale on the heat transfer surfaces, and clogging pipes and manifolds.
1-degree increase in cooling water temperature can cause a 3% increase in energy usage. Proper maintenance could improve a cooling tower’s efficiency.

## Slide 32: General Fundamentals
Common Cooling Tower Problems:
Scaling/Precipitation Fouling:
Mineral based scales that form due to exceeding the saturation point of the scaling species.
Microbiological Fouling or Biofouling:
It may occur from poor or inadequate biocide feed and control.
Deposition/Particulate Fouling (including corrosion products)
Suspended solids such as dirt or corrosion products that settle out in the cooling system.
Goal:
Water is scarce. Thus, there is an imminent need to use water efficiently and treat it within the parameters of environment to make it sustainable.

## Slide 33
Scale and Bio-Removal System
SBR is a fully automatic online technology that continuously clean the cooling tower water and augments the cooling performance and treat cooling water without any chemicals.
Electrolysis Chamber
Media Filterer
Cooling Tower

## Slide 34: Scale and Bio-Removal System
Electrolysis Based Scale Removal and Prevention with Water Disinfection Process
A DC electrical power source is connected to two electrodes typically made from Platinum with Iridium coated (Anode) and Stainless Steel-316 (Cathode) .
Hydrogen will appear at the cathode (where electrons enter the water), oxygen will appear at the anode.
This electrolytic environment creates a high pH level at the cathode, which causes existing mineral salts in the water to precipitate and stick to the cathodes. This prevents them from depositing on the heat exchange surfaces at other parts of the system in the form of scale.
SCRAPPER

## Slide 35: Scale and Bio-Removal System
Due to electrolysis (Cathode and Anodic Reaction) all the TDS (Salts like Calcium, magnesium, Iron) are attracted towards the Cathode(-) and are stick and precipitated to the smooth surface of the Cathode Drum. Deposits are formed due to these salts which are removed in the Cathode drum removed by scrapper mechanism as programmed.
As the water becomes soft the salts are dissolved and the capability of the water to dissolve the salts increases and some precipitation takes places in the drum which is automatically removed during flushing.

## Slide 36: SBR Working Principle
Electrolysis works as follows:
Water in the cycle is pumped into the electrolysis chamber.
The water pH level is raised slightly increasing the alkaline environment causes existing mineral salts in the water to precipitate and stick to the cathodes and prevent corrosion.
Cathode (reduction): 2 H2O(l) + 2e− → H2(g) + 2 OH− (aq)
The main ingredients of scale in water systems (Mg(OH)2, CaCO3, MgCO3, SiO2) are almost completely removed from the water in this process.
At Cathode

## Slide 37: SBR Working Principle
❖SBR implements electrolysis technology that promotes electro-chlorination and electro- oxidation, delivering superior water treatment results in comparison to chemical treatment.
❖The anode oxidation reaction is a series of reactions that produce gases and free radicals with high oxidation potential that disinfects the water.
❖Due to anodic(+) reaction Free chlorine, Hydrogen Peroxide, Carbon Di-oxide, Ozone, Oxygen is evolved which kills the bacterial growth and kills the algae in the cooling tower. Since the free chlorine is available in the water it will stop the algae growth in the cooling tower.
❖Anode (oxidation): 4 OH− (aq) → O2(g) + 2 H2O(l) + 4 e−
❖ The agglomerated suspended solids removed further with a Sand filter/Disc Filter
At Anode

## Slide 38: SBR Working Principle
Disc Filter
The disc filter consists of multiple discs mounted onto a central drum. The woven filter media captures solids and particles, ensuring a continuous flow of clean water.
The innovative backwash cycle optimizes cleaning efficiency.
Made from durable materials like polyester or polypropylene, disc filters have a long service life.
Disc Filter

## Slide 39: Blowdown Water Reduction By 50%
SAVE 50% BLOW DOWN WATER
ZERO CHEMICALS
REDUCE STP TREATMENT COST
IMPROVE COOLING TOWER PERFORMANCE
3 x COC
Israel Technology

## Slide 40: Advantages Of SBR
Save more than 50% of blowdown water.
SBR allows the operation of the cooling towers at 4500-5000 µs conductivity, saving up to 50% of Blow down water.
Zero chemicals that means Elimination of maintenance, storage and discharge of chemicals.
Environment-friendly.
Reduce operational cost.
Reduces your maintenance downtime.
Enhance cooling system performance.
Low operating costs.
Multiply Cycles of Concentration (COC).
By eliminating the use of chemicals, SBR allows the saving of 100% of bleed-off that can be applied for watering or other uses.

## Slide 41: Our Commitments: No harm to People, Environment & Society
Climate Change
Targeting Net Zero by 2050
42% reduction of CO2 to 1.95 tCO2/tcs by FY30, aligned with India’s NDC’s
Increased use of scrap in steelmaking
Adoption of disruptive technologies (Green H2, CCUS, etc.) in a progressive manner
Target reduction for CO2 emissions, specific energy consumption, specific water consumption, specific process dust emissions, SOx and NOx emissions by 2030 is from baseline 2005 levels
Promoting Circular Economy
Focus on ‘Zero waste to Landfill’
‘No net loss’ of Biodiversity by FY30
Increase green cover across operations
Air Emissions
PM, SOx and NOx emission targets of 0.26,
0.82 and 0.91 kg/tcs respectively, by FY30
Adoption of best available technologies like MEROS, Oven Pressure Control, CDQ, TRT etc.
Transition from thermal to RE
19% reduction in specific energy consumption to 5.65 Gcal/tcs by FY30
Energy efficiency and process efficiency improvements through BATs
Energy Transition
Water Security Circularity & Biodiversity
Maintaining zero liquid discharge
39% reduction in specific water consumption to 2.21 m3/tcs by FY30
Adopting digitalisation for better water control and monitoring

## Slide 42: THANK YOU
Avinash Ujjwal
8284853388
avinash.ujjwal@jsw.in